{"text_format":"1","workbook":"xlsx","n_sheets":25,"sheets":["Kalkulering kurser og batteri","K01","K02","K03","K04","K05","K06","K07","K08","K09","K10","K11","K12","K13","K14","K15","K16","K17","K18","K19","K20","K21","K22","K23","K24"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":24,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Kalkulering kurser og batteri","index":0,"n_rows":55,"n_cols":6,"rows_kept":55,"cut":false,"hidden":false,"merged":[[7,1,7,2],[3,1,4,1],[1,1,2,1]]}
[]
[null,{"$f":"IF(E55<=128,\"Behov for 8 kurser\",IF(E55<=288,\"Anbefalles 16 kurser\",IF(E55<=432,\"Anbefales 24 kurser\",IF(E55<=480,\"Anbefales flere sentraler\",\"\"))))","v":"Behov for 8 kurser"},"Samlet Reservekapasitet"]
[null,null,{"$f":"IF(E55>=385,\"\",IF(E55>=257,(480-E55)/480,IF(E55>=129,(320-E55)/320,IF(E55>=1,(160-E55)/160,\"\"))))","v":""}]
[null,{"$f":"IF(E55>=481,\"For mange armaturer. Benytt flere sentraler\",IF(E55>=321,\"Minste behov 24 kurser\",IF(E55>=161,\"Minste behov 16 kurser\",IF(E55>=145,\"Minste behov 8 kurser\",\"\"))))","v":""},"Samlet Reservekapasitet"]
[null,null,{"$f":"IF(E55>=481,\"\",IF(E55>=321,(480-E55)/480,IF(E55>=161,(320-E55)/320,IF(E55>=145,(160-E55)/160,\"\"))))","v":""}]
[null,{"$f":"IF(E55>480,\"Minimum behov for antall kurser\",\"\")","v":""},{"$f":"IF(E55>480,ROUNDUP(E55/20,0),\"\")","v":""}]
[null,{"$f":"IF(E55>384,\"Anbefalt behov for antall kurser\",\"\")","v":""},{"$f":"IF(E55>384,ROUNDUP(E55/16,0),\"\")","v":""}]
[null,{"$f":"IF(E54<=680,\"7.5 Ah batterier og 1 batteriskap\",IF(E54<=1920,\"18 Ah batterier og 1 batteriskap\",IF(E54<=2700,\"26 Ah batterier og 2 batteriskap\",\"For høy effekt. Benytt flere sentraler\")))","v":"7.5 Ah batterier og 1 batteriskap"}]
[null,"Antall lamper totalt for sentral","Produkttype"]
[null,null,"ESC / SAFE 29",4.5999999999999996,{"$f":"B10*D10","v":0}]
[null,null,"ESC 90",4.2,{"$f":"B11*D11","v":0}]
[null,null,"ESC 80",4.2,0]
[null,null,"ESC 81",4.2,0]
[null,null,"ESC 10",4.5999999999999996,0]
[null,null,"SILVER",6.5,0]
[null,null,"ESC 3 70m",18,0]
[null,null,"ESC 3 120m",32,0]
[null,null,"SOLID EXIT",3,0]
[null,null,"SOLID EXIT 2",3,0]
[null,null,"ROBUST EXIT",4.5999999999999996,0]
[null,null,"COMBO",3.4,0]
[null,null,"FIND",3.5,0]
[null,null,"HEAVY EXIT",4.5999999999999996,0]
[null,null,"STEEL",5.0999999999999996,0]
[null,null,"PLUS",4.7,0]
[null,null,"LINESPOT II LOWBAY",5.5,0]
[null,null,"ZONESPOT II LOWBAY",5.5,0]
[null,null,"LINESPOT II MIDBAY",9.5,0]
[null,null,"ZONESPOT II MIDBAY",9.5,0]
[null,null,"ZONESPOT II HIGHBAY",9.5,0]
[null,null,"ESC / SAFE 29",4.5999999999999996,0]
[null,null,"SAFE 82",18,0]
[null,null,"SAFE 6",7.5,0]
[null,null,"TRISPOT",9.5,0]
[null,null,"SLIMSPOT",5.5,0]
[null,null,"LINESPOT",5.5,0]
[null,null,"SOLID ZONE",8.5,0]
[null,null,"SOLID LINE",6,0]
[null,null,"ROBUST 86",18,0]
[null,null,"SLIMSPOT LINE LOWBAY",5.5,0]
[null,null,"SLIMSPOT LINE MIDBAY",5.5,0]
[null,null,"SLIMSPOT ZONE LOWBAY",5.5,0]
[null,null,"SLIMSPOT ZONE MIDBAY",5.5,0]
[null,null,"STEP",5.5,0]
[null,null,"STAMINA ZONE",8.5,0]
[null,null,"STAMINA ZONE HIGHOUTPUT",18.5,0]
[null,null,"STAMINA LINE LOWBAY",6,0]
[null,null,"STAMINA LINE MIDBAY",6,0]
[null,null,"SMOOTH",5.5,0]
[null,null,"LYSKASTER 30W",30,0]
[]
[null,"ANTALL 3RD","3RD PART?",null,null,"WATT 3RD"]
[null,null,"NAVN 3PART",{"$f":"F53","v":50},0,50]
[null,null,null,null,{"$f":"SUM(E10:E53)","v":0}]
[null,null,null,null,{"$f":"SUM(B10:B50)+B53","v":0}]

{"sheet":"K01","index":1,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["01",".01","L","01.01","  ML  / LL"]
["01",".02","L","01.02","  ML  / LL"]
["01",".03","L","01.03","  ML  / LL"]
["01",".04","L","01.04","  ML  / LL"]
["01",".05","L","01.05","  ML  / LL"]
["01",".06","L","01.06","  ML  / LL"]
["01",".07","L","01.07","  ML  / LL"]
["01",".08","L","01.08","  ML  / LL"]
["01",".09","L","01.09","  ML  / LL"]
["01",".10","L","01.10","  ML  / LL"]
["01",".11","L","01.11","  ML  / LL"]
["01",".12","L","01.12","  ML  / LL"]
["01",".13","L","01.13","  ML  / LL"]
["01",".14","L","01.14","  ML  / LL"]
["01",".15","L","01.15","  ML  / LL"]
["01",".16","L","01.16","  ML  / LL"]
["01",".01","H","01.17","  ML  / LL"]
["01",".02","H","01.18","  ML  / LL"]
["01",".03","H","01.19","  ML  / LL"]
["01",".04","H","01.20","  ML  / LL"]
["01",".05","H","01.21","  ML  / LL"]
["01",".06","H","01.22","  ML  / LL"]
["01",".07","H","01.23","  ML  / LL"]
["01",".08","H","01.24","  ML  / LL"]
["01",".09","H","01.25","  ML  / LL"]
["01",".10","H","01.26","  ML  / LL"]
["01",".11","H","01.27","  ML  / LL"]
["01",".12","H","01.28","  ML  / LL"]
["01",".13","H","01.29","  ML  / LL"]
["01",".14","H","01.30","  ML  / LL"]
["01",".15","H","01.31","  ML  / LL"]
["01",".16","H","01.32","  ML  / LL"]

{"sheet":"K02","index":2,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["02",".01","L","02.01","  ML  / LL"]
["02",".02","L","02.02","  ML  / LL"]
["02",".03","L","02.03","  ML  / LL"]
["02",".04","L","02.04","  ML  / LL"]
["02",".05","L","02.05","  ML  / LL"]
["02",".06","L","02.06","  ML  / LL"]
["02",".07","L","02.07","  ML  / LL"]
["02",".08","L","02.08","  ML  / LL"]
["02",".09","L","02.09","  ML  / LL"]
["02",".10","L","02.10","  ML  / LL"]
["02",".11","L","02.11","  ML  / LL"]
["02",".12","L","02.12","  ML  / LL"]
["02",".13","L","02.13","  ML  / LL"]
["02",".14","L","02.14","  ML  / LL"]
["02",".15","L","02.15","  ML  / LL"]
["02",".16","L","02.16","  ML  / LL"]
["02",".01","H","02.17","  ML  / LL"]
["02",".02","H","02.18","  ML  / LL"]
["02",".03","H","02.19","  ML  / LL"]
["02",".04","H","02.20","  ML  / LL"]
["02",".05","H","02.21","  ML  / LL"]
["02",".06","H","02.22","  ML  / LL"]
["02",".07","H","02.23","  ML  / LL"]
["02",".08","H","02.24","  ML  / LL"]
["02",".09","H","02.25","  ML  / LL"]
["02",".10","H","02.26","  ML  / LL"]
["02",".11","H","02.27","  ML  / LL"]
["02",".12","H","02.28","  ML  / LL"]
["02",".13","H","02.29","  ML  / LL"]
["02",".14","H","02.30","  ML  / LL"]
["02",".15","H","02.31","  ML  / LL"]
["02",".16","H","02.32","  ML  / LL"]

{"sheet":"K03","index":3,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["03",".01","L","03.01","  ML  / LL"]
["03",".02","L","03.02","  ML  / LL"]
["03",".03","L","03.03","  ML  / LL"]
["03",".04","L","03.04","  ML  / LL"]
["03",".05","L","03.05","  ML  / LL"]
["03",".06","L","03.06","  ML  / LL"]
["03",".07","L","03.07","  ML  / LL"]
["03",".08","L","03.08","  ML  / LL"]
["03",".09","L","03.09","  ML  / LL"]
["03",".10","L","03.10","  ML  / LL"]
["03",".11","L","03.11","  ML  / LL"]
["03",".12","L","03.12","  ML  / LL"]
["03",".13","L","03.13","  ML  / LL"]
["03",".14","L","03.14","  ML  / LL"]
["03",".15","L","03.15","  ML  / LL"]
["03",".16","L","03.16","  ML  / LL"]
["03",".01","H","03.17","  ML  / LL"]
["03",".02","H","03.18","  ML  / LL"]
["03",".03","H","03.19","  ML  / LL"]
["03",".04","H","03.20","  ML  / LL"]
["03",".05","H","03.21","  ML  / LL"]
["03",".06","H","03.22","  ML  / LL"]
["03",".07","H","03.23","  ML  / LL"]
["03",".08","H","03.24","  ML  / LL"]
["03",".09","H","03.25","  ML  / LL"]
["03",".10","H","03.26","  ML  / LL"]
["03",".11","H","03.27","  ML  / LL"]
["03",".12","H","03.28","  ML  / LL"]
["03",".13","H","03.29","  ML  / LL"]
["03",".14","H","03.30","  ML  / LL"]
["03",".15","H","03.31","  ML  / LL"]
["03",".16","H","03.32","  ML  / LL"]

{"sheet":"K04","index":4,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["04",".01","L","04.01","  ML  / LL"]
["04",".02","L","04.02","  ML  / LL"]
["04",".03","L","04.03","  ML  / LL"]
["04",".04","L","04.04","  ML  / LL"]
["04",".05","L","04.05","  ML  / LL"]
["04",".06","L","04.06","  ML  / LL"]
["04",".07","L","04.07","  ML  / LL"]
["04",".08","L","04.08","  ML  / LL"]
["04",".09","L","04.09","  ML  / LL"]
["04",".10","L","04.10","  ML  / LL"]
["04",".11","L","04.11","  ML  / LL"]
["04",".12","L","04.12","  ML  / LL"]
["04",".13","L","04.13","  ML  / LL"]
["04",".14","L","04.14","  ML  / LL"]
["04",".15","L","04.15","  ML  / LL"]
["04",".16","L","04.16","  ML  / LL"]
["04",".01","H","04.17","  ML  / LL"]
["04",".02","H","04.18","  ML  / LL"]
["04",".03","H","04.19","  ML  / LL"]
["04",".04","H","04.20","  ML  / LL"]
["04",".05","H","04.21","  ML  / LL"]
["04",".06","H","04.22","  ML  / LL"]
["04",".07","H","04.23","  ML  / LL"]
["04",".08","H","04.24","  ML  / LL"]
["04",".09","H","04.25","  ML  / LL"]
["04",".10","H","04.26","  ML  / LL"]
["04",".11","H","04.27","  ML  / LL"]
["04",".12","H","04.28","  ML  / LL"]
["04",".13","H","04.29","  ML  / LL"]
["04",".14","H","04.30","  ML  / LL"]
["04",".15","H","04.31","  ML  / LL"]
["04",".16","H","04.32","  ML  / LL"]

{"sheet":"K05","index":5,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["05",".01","L","05.01","  ML  / LL"]
["05",".02","L","05.02","  ML  / LL"]
["05",".03","L","05.03","  ML  / LL"]
["05",".04","L","05.04","  ML  / LL"]
["05",".05","L","05.05","  ML  / LL"]
["05",".06","L","05.06","  ML  / LL"]
["05",".07","L","05.07","  ML  / LL"]
["05",".08","L","05.08","  ML  / LL"]
["05",".09","L","05.09","  ML  / LL"]
["05",".10","L","05.10","  ML  / LL"]
["05",".11","L","05.11","  ML  / LL"]
["05",".12","L","05.12","  ML  / LL"]
["05",".13","L","05.13","  ML  / LL"]
["05",".14","L","05.14","  ML  / LL"]
["05",".15","L","05.15","  ML  / LL"]
["05",".16","L","05.16","  ML  / LL"]
["05",".01","H","05.17","  ML  / LL"]
["05",".02","H","05.18","  ML  / LL"]
["05",".03","H","05.19","  ML  / LL"]
["05",".04","H","05.20","  ML  / LL"]
["05",".05","H","05.21","  ML  / LL"]
["05",".06","H","05.22","  ML  / LL"]
["05",".07","H","05.23","  ML  / LL"]
["05",".08","H","05.24","  ML  / LL"]
["05",".09","H","05.25","  ML  / LL"]
["05",".10","H","05.26","  ML  / LL"]
["05",".11","H","05.27","  ML  / LL"]
["05",".12","H","05.28","  ML  / LL"]
["05",".13","H","05.29","  ML  / LL"]
["05",".14","H","05.30","  ML  / LL"]
["05",".15","H","05.31","  ML  / LL"]
["05",".16","H","05.32","  ML  / LL"]

{"sheet":"K06","index":6,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["06",".01","L","06.01","  ML  / LL"]
["06",".02","L","06.02","  ML  / LL"]
["06",".03","L","06.03","  ML  / LL"]
["06",".04","L","06.04","  ML  / LL"]
["06",".05","L","06.05","  ML  / LL"]
["06",".06","L","06.06","  ML  / LL"]
["06",".07","L","06.07","  ML  / LL"]
["06",".08","L","06.08","  ML  / LL"]
["06",".09","L","06.09","  ML  / LL"]
["06",".10","L","06.10","  ML  / LL"]
["06",".11","L","06.11","  ML  / LL"]
["06",".12","L","06.12","  ML  / LL"]
["06",".13","L","06.13","  ML  / LL"]
["06",".14","L","06.14","  ML  / LL"]
["06",".15","L","06.15","  ML  / LL"]
["06",".16","L","06.16","  ML  / LL"]
["06",".01","H","06.17","  ML  / LL"]
["06",".02","H","06.18","  ML  / LL"]
["06",".03","H","06.19","  ML  / LL"]
["06",".04","H","06.20","  ML  / LL"]
["06",".05","H","06.21","  ML  / LL"]
["06",".06","H","06.22","  ML  / LL"]
["06",".07","H","06.23","  ML  / LL"]
["06",".08","H","06.24","  ML  / LL"]
["06",".09","H","06.25","  ML  / LL"]
["06",".10","H","06.26","  ML  / LL"]
["06",".11","H","06.27","  ML  / LL"]
["06",".12","H","06.28","  ML  / LL"]
["06",".13","H","06.29","  ML  / LL"]
["06",".14","H","06.30","  ML  / LL"]
["06",".15","H","06.31","  ML  / LL"]
["06",".16","H","06.32","  ML  / LL"]

{"sheet":"K07","index":7,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["07",".01","L","07.01","  ML  / LL"]
["07",".02","L","07.02","  ML  / LL"]
["07",".03","L","07.03","  ML  / LL"]
["07",".04","L","07.04","  ML  / LL"]
["07",".05","L","07.05","  ML  / LL"]
["07",".06","L","07.06","  ML  / LL"]
["07",".07","L","07.07","  ML  / LL"]
["07",".08","L","07.08","  ML  / LL"]
["07",".09","L","07.09","  ML  / LL"]
["07",".10","L","07.10","  ML  / LL"]
["07",".11","L","07.11","  ML  / LL"]
["07",".12","L","07.12","  ML  / LL"]
["07",".13","L","07.13","  ML  / LL"]
["07",".14","L","07.14","  ML  / LL"]
["07",".15","L","07.15","  ML  / LL"]
["07",".16","L","07.16","  ML  / LL"]
["07",".01","H","07.17","  ML  / LL"]
["07",".02","H","07.18","  ML  / LL"]
["07",".03","H","07.19","  ML  / LL"]
["07",".04","H","07.20","  ML  / LL"]
["07",".05","H","07.21","  ML  / LL"]
["07",".06","H","07.22","  ML  / LL"]
["07",".07","H","07.23","  ML  / LL"]
["07",".08","H","07.24","  ML  / LL"]
["07",".09","H","07.25","  ML  / LL"]
["07",".10","H","07.26","  ML  / LL"]
["07",".11","H","07.27","  ML  / LL"]
["07",".12","H","07.28","  ML  / LL"]
["07",".13","H","07.29","  ML  / LL"]
["07",".14","H","07.30","  ML  / LL"]
["07",".15","H","07.31","  ML  / LL"]
["07",".16","H","07.32","  ML  / LL"]

{"sheet":"K08","index":8,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["08",".01","L","08.01","  ML  / LL"]
["08",".02","L","08.02","  ML  / LL"]
["08",".03","L","08.03","  ML  / LL"]
["08",".04","L","08.04","  ML  / LL"]
["08",".05","L","08.05","  ML  / LL"]
["08",".06","L","08.06","  ML  / LL"]
["08",".07","L","08.07","  ML  / LL"]
["08",".08","L","08.08","  ML  / LL"]
["08",".09","L","08.09","  ML  / LL"]
["08",".10","L","08.10","  ML  / LL"]
["08",".11","L","08.11","  ML  / LL"]
["08",".12","L","08.12","  ML  / LL"]
["08",".13","L","08.13","  ML  / LL"]
["08",".14","L","08.14","  ML  / LL"]
["08",".15","L","08.15","  ML  / LL"]
["08",".16","L","08.16","  ML  / LL"]
["08",".01","H","08.17","  ML  / LL"]
["08",".02","H","08.18","  ML  / LL"]
["08",".03","H","08.19","  ML  / LL"]
["08",".04","H","08.20","  ML  / LL"]
["08",".05","H","08.21","  ML  / LL"]
["08",".06","H","08.22","  ML  / LL"]
["08",".07","H","08.23","  ML  / LL"]
["08",".08","H","08.24","  ML  / LL"]
["08",".09","H","08.25","  ML  / LL"]
["08",".10","H","08.26","  ML  / LL"]
["08",".11","H","08.27","  ML  / LL"]
["08",".12","H","08.28","  ML  / LL"]
["08",".13","H","08.29","  ML  / LL"]
["08",".14","H","08.30","  ML  / LL"]
["08",".15","H","08.31","  ML  / LL"]
["08",".16","H","08.32","  ML  / LL"]

{"sheet":"K09","index":9,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["09",".01","L","09.01","  ML  / LL"]
["09",".02","L","09.02","  ML  / LL"]
["09",".03","L","09.03","  ML  / LL"]
["09",".04","L","09.04","  ML  / LL"]
["09",".05","L","09.05","  ML  / LL"]
["09",".06","L","09.06","  ML  / LL"]
["09",".07","L","09.07","  ML  / LL"]
["09",".08","L","09.08","  ML  / LL"]
["09",".09","L","09.09","  ML  / LL"]
["09",".10","L","09.10","  ML  / LL"]
["09",".11","L","09.11","  ML  / LL"]
["09",".12","L","09.12","  ML  / LL"]
["09",".13","L","09.13","  ML  / LL"]
["09",".14","L","09.14","  ML  / LL"]
["09",".15","L","09.15","  ML  / LL"]
["09",".16","L","09.16","  ML  / LL"]
["09",".01","H","09.17","  ML  / LL"]
["09",".02","H","09.18","  ML  / LL"]
["09",".03","H","09.19","  ML  / LL"]
["09",".04","H","09.20","  ML  / LL"]
["09",".05","H","09.21","  ML  / LL"]
["09",".06","H","09.22","  ML  / LL"]
["09",".07","H","09.23","  ML  / LL"]
["09",".08","H","09.24","  ML  / LL"]
["09",".09","H","09.25","  ML  / LL"]
["09",".10","H","09.26","  ML  / LL"]
["09",".11","H","09.27","  ML  / LL"]
["09",".12","H","09.28","  ML  / LL"]
["09",".13","H","09.29","  ML  / LL"]
["09",".14","H","09.30","  ML  / LL"]
["09",".15","H","09.31","  ML  / LL"]
["09",".16","H","09.32","  ML  / LL"]

{"sheet":"K10","index":10,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["10",".01","L","10.01","  ML  / LL"]
["10",".02","L","10.02","  ML  / LL"]
["10",".03","L","10.03","  ML  / LL"]
["10",".04","L","10.04","  ML  / LL"]
["10",".05","L","10.05","  ML  / LL"]
["10",".06","L","10.06","  ML  / LL"]
["10",".07","L","10.07","  ML  / LL"]
["10",".08","L","10.08","  ML  / LL"]
["10",".09","L","10.09","  ML  / LL"]
["10",".10","L","10.10","  ML  / LL"]
["10",".11","L","10.11","  ML  / LL"]
["10",".12","L","10.12","  ML  / LL"]
["10",".13","L","10.13","  ML  / LL"]
["10",".14","L","10.14","  ML  / LL"]
["10",".15","L","10.15","  ML  / LL"]
["10",".16","L","10.16","  ML  / LL"]
["10",".01","H","10.17","  ML  / LL"]
["10",".02","H","10.18","  ML  / LL"]
["10",".03","H","10.19","  ML  / LL"]
["10",".04","H","10.20","  ML  / LL"]
["10",".05","H","10.21","  ML  / LL"]
["10",".06","H","10.22","  ML  / LL"]
["10",".07","H","10.23","  ML  / LL"]
["10",".08","H","10.24","  ML  / LL"]
["10",".09","H","10.25","  ML  / LL"]
["10",".10","H","10.26","  ML  / LL"]
["10",".11","H","10.27","  ML  / LL"]
["10",".12","H","10.28","  ML  / LL"]
["10",".13","H","10.29","  ML  / LL"]
["10",".14","H","10.30","  ML  / LL"]
["10",".15","H","10.31","  ML  / LL"]
["10",".16","H","10.32","  ML  / LL"]

{"sheet":"K11","index":11,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["11",".01","L","11.01","  ML  / LL"]
["11",".02","L","11.02","  ML  / LL"]
["11",".03","L","11.03","  ML  / LL"]
["11",".04","L","11.04","  ML  / LL"]
["11",".05","L","11.05","  ML  / LL"]
["11",".06","L","11.06","  ML  / LL"]
["11",".07","L","11.07","  ML  / LL"]
["11",".08","L","11.08","  ML  / LL"]
["11",".09","L","11.09","  ML  / LL"]
["11",".10","L","11.10","  ML  / LL"]
["11",".11","L","11.11","  ML  / LL"]
["11",".12","L","11.12","  ML  / LL"]
["11",".13","L","11.13","  ML  / LL"]
["11",".14","L","11.14","  ML  / LL"]
["11",".15","L","11.15","  ML  / LL"]
["11",".16","L","11.16","  ML  / LL"]
["11",".01","H","11.17","  ML  / LL"]
["11",".02","H","11.18","  ML  / LL"]
["11",".03","H","11.19","  ML  / LL"]
["11",".04","H","11.20","  ML  / LL"]
["11",".05","H","11.21","  ML  / LL"]
["11",".06","H","11.22","  ML  / LL"]
["11",".07","H","11.23","  ML  / LL"]
["11",".08","H","11.24","  ML  / LL"]
["11",".09","H","11.25","  ML  / LL"]
["11",".10","H","11.26","  ML  / LL"]
["11",".11","H","11.27","  ML  / LL"]
["11",".12","H","11.28","  ML  / LL"]
["11",".13","H","11.29","  ML  / LL"]
["11",".14","H","11.30","  ML  / LL"]
["11",".15","H","11.31","  ML  / LL"]
["11",".16","H","11.32","  ML  / LL"]

{"sheet":"K12","index":12,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["12",".01","L","12.01","  ML  / LL"]
["12",".02","L","12.02","  ML  / LL"]
["12",".03","L","12.03","  ML  / LL"]
["12",".04","L","12.04","  ML  / LL"]
["12",".05","L","12.05","  ML  / LL"]
["12",".06","L","12.06","  ML  / LL"]
["12",".07","L","12.07","  ML  / LL"]
["12",".08","L","12.08","  ML  / LL"]
["12",".09","L","12.09","  ML  / LL"]
["12",".10","L","12.10","  ML  / LL"]
["12",".11","L","12.11","  ML  / LL"]
["12",".12","L","12.12","  ML  / LL"]
["12",".13","L","12.13","  ML  / LL"]
["12",".14","L","12.14","  ML  / LL"]
["12",".15","L","12.15","  ML  / LL"]
["12",".16","L","12.16","  ML  / LL"]
["12",".01","H","12.17","  ML  / LL"]
["12",".02","H","12.18","  ML  / LL"]
["12",".03","H","12.19","  ML  / LL"]
["12",".04","H","12.20","  ML  / LL"]
["12",".05","H","12.21","  ML  / LL"]
["12",".06","H","12.22","  ML  / LL"]
["12",".07","H","12.23","  ML  / LL"]
["12",".08","H","12.24","  ML  / LL"]
["12",".09","H","12.25","  ML  / LL"]
["12",".10","H","12.26","  ML  / LL"]
["12",".11","H","12.27","  ML  / LL"]
["12",".12","H","12.28","  ML  / LL"]
["12",".13","H","12.29","  ML  / LL"]
["12",".14","H","12.30","  ML  / LL"]
["12",".15","H","12.31","  ML  / LL"]
["12",".16","H","12.32","  ML  / LL"]

{"sheet":"K13","index":13,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["13",".01","L","13.01","  ML  / LL"]
["13",".02","L","13.02","  ML  / LL"]
["13",".03","L","13.03","  ML  / LL"]
["13",".04","L","13.04","  ML  / LL"]
["13",".05","L","13.05","  ML  / LL"]
["13",".06","L","13.06","  ML  / LL"]
["13",".07","L","13.07","  ML  / LL"]
["13",".08","L","13.08","  ML  / LL"]
["13",".09","L","13.09","  ML  / LL"]
["13",".10","L","13.10","  ML  / LL"]
["13",".11","L","13.11","  ML  / LL"]
["13",".12","L","13.12","  ML  / LL"]
["13",".13","L","13.13","  ML  / LL"]
["13",".14","L","13.14","  ML  / LL"]
["13",".15","L","13.15","  ML  / LL"]
["13",".16","L","13.16","  ML  / LL"]
["13",".01","H","13.17","  ML  / LL"]
["13",".02","H","13.18","  ML  / LL"]
["13",".03","H","13.19","  ML  / LL"]
["13",".04","H","13.20","  ML  / LL"]
["13",".05","H","13.21","  ML  / LL"]
["13",".06","H","13.22","  ML  / LL"]
["13",".07","H","13.23","  ML  / LL"]
["13",".08","H","13.24","  ML  / LL"]
["13",".09","H","13.25","  ML  / LL"]
["13",".10","H","13.26","  ML  / LL"]
["13",".11","H","13.27","  ML  / LL"]
["13",".12","H","13.28","  ML  / LL"]
["13",".13","H","13.29","  ML  / LL"]
["13",".14","H","13.30","  ML  / LL"]
["13",".15","H","13.31","  ML  / LL"]
["13",".16","H","13.32","  ML  / LL"]

{"sheet":"K14","index":14,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["14",".01","L","14.01","  ML  / LL"]
["14",".02","L","14.02","  ML  / LL"]
["14",".03","L","14.03","  ML  / LL"]
["14",".04","L","14.04","  ML  / LL"]
["14",".05","L","14.05","  ML  / LL"]
["14",".06","L","14.06","  ML  / LL"]
["14",".07","L","14.07","  ML  / LL"]
["14",".08","L","14.08","  ML  / LL"]
["14",".09","L","14.09","  ML  / LL"]
["14",".10","L","14.10","  ML  / LL"]
["14",".11","L","14.11","  ML  / LL"]
["14",".12","L","14.12","  ML  / LL"]
["14",".13","L","14.13","  ML  / LL"]
["14",".14","L","14.14","  ML  / LL"]
["14",".15","L","14.15","  ML  / LL"]
["14",".16","L","14.16","  ML  / LL"]
["14",".01","H","14.17","  ML  / LL"]
["14",".02","H","14.18","  ML  / LL"]
["14",".03","H","14.19","  ML  / LL"]
["14",".04","H","14.20","  ML  / LL"]
["14",".05","H","14.21","  ML  / LL"]
["14",".06","H","14.22","  ML  / LL"]
["14",".07","H","14.23","  ML  / LL"]
["14",".08","H","14.24","  ML  / LL"]
["14",".09","H","14.25","  ML  / LL"]
["14",".10","H","14.26","  ML  / LL"]
["14",".11","H","14.27","  ML  / LL"]
["14",".12","H","14.28","  ML  / LL"]
["14",".13","H","14.29","  ML  / LL"]
["14",".14","H","14.30","  ML  / LL"]
["14",".15","H","14.31","  ML  / LL"]
["14",".16","H","14.32","  ML  / LL"]

{"sheet":"K15","index":15,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["15",".01","L","15.01","  ML  / LL"]
["15",".02","L","15.02","  ML  / LL"]
["15",".03","L","15.03","  ML  / LL"]
["15",".04","L","15.04","  ML  / LL"]
["15",".05","L","15.05","  ML  / LL"]
["15",".06","L","15.06","  ML  / LL"]
["15",".07","L","15.07","  ML  / LL"]
["15",".08","L","15.08","  ML  / LL"]
["15",".09","L","15.09","  ML  / LL"]
["15",".10","L","15.10","  ML  / LL"]
["15",".11","L","15.11","  ML  / LL"]
["15",".12","L","15.12","  ML  / LL"]
["15",".13","L","15.13","  ML  / LL"]
["15",".14","L","15.14","  ML  / LL"]
["15",".15","L","15.15","  ML  / LL"]
["15",".16","L","15.16","  ML  / LL"]
["15",".01","H","15.17","  ML  / LL"]
["15",".02","H","15.18","  ML  / LL"]
["15",".03","H","15.19","  ML  / LL"]
["15",".04","H","15.20","  ML  / LL"]
["15",".05","H","15.21","  ML  / LL"]
["15",".06","H","15.22","  ML  / LL"]
["15",".07","H","15.23","  ML  / LL"]
["15",".08","H","15.24","  ML  / LL"]
["15",".09","H","15.25","  ML  / LL"]
["15",".10","H","15.26","  ML  / LL"]
["15",".11","H","15.27","  ML  / LL"]
["15",".12","H","15.28","  ML  / LL"]
["15",".13","H","15.29","  ML  / LL"]
["15",".14","H","15.30","  ML  / LL"]
["15",".15","H","15.31","  ML  / LL"]
["15",".16","H","15.32","  ML  / LL"]

{"sheet":"K16","index":16,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["16",".01","L","16.01","  ML  / LL"]
["16",".02","L","16.02","  ML  / LL"]
["16",".03","L","16.03","  ML  / LL"]
["16",".04","L","16.04","  ML  / LL"]
["16",".05","L","16.05","  ML  / LL"]
["16",".06","L","16.06","  ML  / LL"]
["16",".07","L","16.07","  ML  / LL"]
["16",".08","L","16.08","  ML  / LL"]
["16",".09","L","16.09","  ML  / LL"]
["16",".10","L","16.10","  ML  / LL"]
["16",".11","L","16.11","  ML  / LL"]
["16",".12","L","16.12","  ML  / LL"]
["16",".13","L","16.13","  ML  / LL"]
["16",".14","L","16.14","  ML  / LL"]
["16",".15","L","16.15","  ML  / LL"]
["16",".16","L","16.16","  ML  / LL"]
["16",".01","H","16.17","  ML  / LL"]
["16",".02","H","16.18","  ML  / LL"]
["16",".03","H","16.19","  ML  / LL"]
["16",".04","H","16.20","  ML  / LL"]
["16",".05","H","16.21","  ML  / LL"]
["16",".06","H","16.22","  ML  / LL"]
["16",".07","H","16.23","  ML  / LL"]
["16",".08","H","16.24","  ML  / LL"]
["16",".09","H","16.25","  ML  / LL"]
["16",".10","H","16.26","  ML  / LL"]
["16",".11","H","16.27","  ML  / LL"]
["16",".12","H","16.28","  ML  / LL"]
["16",".13","H","16.29","  ML  / LL"]
["16",".14","H","16.30","  ML  / LL"]
["16",".15","H","16.31","  ML  / LL"]
["16",".16","H","16.32","  ML  / LL"]

{"sheet":"K17","index":17,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["17",".01","L","17.01","  ML  / LL"]
["17",".02","L","17.02","  ML  / LL"]
["17",".03","L","17.03","  ML  / LL"]
["17",".04","L","17.04","  ML  / LL"]
["17",".05","L","17.05","  ML  / LL"]
["17",".06","L","17.06","  ML  / LL"]
["17",".07","L","17.07","  ML  / LL"]
["17",".08","L","17.08","  ML  / LL"]
["17",".09","L","17.09","  ML  / LL"]
["17",".10","L","17.10","  ML  / LL"]
["17",".11","L","17.11","  ML  / LL"]
["17",".12","L","17.12","  ML  / LL"]
["17",".13","L","17.13","  ML  / LL"]
["17",".14","L","17.14","  ML  / LL"]
["17",".15","L","17.15","  ML  / LL"]
["17",".16","L","17.16","  ML  / LL"]
["17",".01","H","17.17","  ML  / LL"]
["17",".02","H","17.18","  ML  / LL"]
["17",".03","H","17.19","  ML  / LL"]
["17",".04","H","17.20","  ML  / LL"]
["17",".05","H","17.21","  ML  / LL"]
["17",".06","H","17.22","  ML  / LL"]
["17",".07","H","17.23","  ML  / LL"]
["17",".08","H","17.24","  ML  / LL"]
["17",".09","H","17.25","  ML  / LL"]
["17",".10","H","17.26","  ML  / LL"]
["17",".11","H","17.27","  ML  / LL"]
["17",".12","H","17.28","  ML  / LL"]
["17",".13","H","17.29","  ML  / LL"]
["17",".14","H","17.30","  ML  / LL"]
["17",".15","H","17.31","  ML  / LL"]
["17",".16","H","17.32","  ML  / LL"]

{"sheet":"K18","index":18,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["18",".01","L","18.01","  ML  / LL"]
["18",".02","L","18.02","  ML  / LL"]
["18",".03","L","18.03","  ML  / LL"]
["18",".04","L","18.04","  ML  / LL"]
["18",".05","L","18.05","  ML  / LL"]
["18",".06","L","18.06","  ML  / LL"]
["18",".07","L","18.07","  ML  / LL"]
["18",".08","L","18.08","  ML  / LL"]
["18",".09","L","18.09","  ML  / LL"]
["18",".10","L","18.10","  ML  / LL"]
["18",".11","L","18.11","  ML  / LL"]
["18",".12","L","18.12","  ML  / LL"]
["18",".13","L","18.13","  ML  / LL"]
["18",".14","L","18.14","  ML  / LL"]
["18",".15","L","18.15","  ML  / LL"]
["18",".16","L","18.16","  ML  / LL"]
["18",".01","H","18.17","  ML  / LL"]
["18",".02","H","18.18","  ML  / LL"]
["18",".03","H","18.19","  ML  / LL"]
["18",".04","H","18.20","  ML  / LL"]
["18",".05","H","18.21","  ML  / LL"]
["18",".06","H","18.22","  ML  / LL"]
["18",".07","H","18.23","  ML  / LL"]
["18",".08","H","18.24","  ML  / LL"]
["18",".09","H","18.25","  ML  / LL"]
["18",".10","H","18.26","  ML  / LL"]
["18",".11","H","18.27","  ML  / LL"]
["18",".12","H","18.28","  ML  / LL"]
["18",".13","H","18.29","  ML  / LL"]
["18",".14","H","18.30","  ML  / LL"]
["18",".15","H","18.31","  ML  / LL"]
["18",".16","H","18.32","  ML  / LL"]

{"sheet":"K19","index":19,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["19",".01","L","19.01","  ML  / LL"]
["19",".02","L","19.02","  ML  / LL"]
["19",".03","L","19.03","  ML  / LL"]
["19",".04","L","19.04","  ML  / LL"]
["19",".05","L","19.05","  ML  / LL"]
["19",".06","L","19.06","  ML  / LL"]
["19",".07","L","19.07","  ML  / LL"]
["19",".08","L","19.08","  ML  / LL"]
["19",".09","L","19.09","  ML  / LL"]
["19",".10","L","19.10","  ML  / LL"]
["19",".11","L","19.11","  ML  / LL"]
["19",".12","L","19.12","  ML  / LL"]
["19",".13","L","19.13","  ML  / LL"]
["19",".14","L","19.14","  ML  / LL"]
["19",".15","L","19.15","  ML  / LL"]
["19",".16","L","19.16","  ML  / LL"]
["19",".01","H","19.17","  ML  / LL"]
["19",".02","H","19.18","  ML  / LL"]
["19",".03","H","19.19","  ML  / LL"]
["19",".04","H","19.20","  ML  / LL"]
["19",".05","H","19.21","  ML  / LL"]
["19",".06","H","19.22","  ML  / LL"]
["19",".07","H","19.23","  ML  / LL"]
["19",".08","H","19.24","  ML  / LL"]
["19",".09","H","19.25","  ML  / LL"]
["19",".10","H","19.26","  ML  / LL"]
["19",".11","H","19.27","  ML  / LL"]
["19",".12","H","19.28","  ML  / LL"]
["19",".13","H","19.29","  ML  / LL"]
["19",".14","H","19.30","  ML  / LL"]
["19",".15","H","19.31","  ML  / LL"]
["19",".16","H","19.32","  ML  / LL"]

{"sheet":"K20","index":20,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["20",".01","L","20.01","  ML  / LL"]
["20",".02","L","20.02","  ML  / LL"]
["20",".03","L","20.03","  ML  / LL"]
["20",".04","L","20.04","  ML  / LL"]
["20",".05","L","20.05","  ML  / LL"]
["20",".06","L","20.06","  ML  / LL"]
["20",".07","L","20.07","  ML  / LL"]
["20",".08","L","20.08","  ML  / LL"]
["20",".09","L","20.09","  ML  / LL"]
["20",".10","L","20.10","  ML  / LL"]
["20",".11","L","20.11","  ML  / LL"]
["20",".12","L","20.12","  ML  / LL"]
["20",".13","L","20.13","  ML  / LL"]
["20",".14","L","20.14","  ML  / LL"]
["20",".15","L","20.15","  ML  / LL"]
["20",".16","L","20.16","  ML  / LL"]
["20",".01","H","20.17","  ML  / LL"]
["20",".02","H","20.18","  ML  / LL"]
["20",".03","H","20.19","  ML  / LL"]
["20",".04","H","20.20","  ML  / LL"]
["20",".05","H","20.21","  ML  / LL"]
["20",".06","H","20.22","  ML  / LL"]
["20",".07","H","20.23","  ML  / LL"]
["20",".08","H","20.24","  ML  / LL"]
["20",".09","H","20.25","  ML  / LL"]
["20",".10","H","20.26","  ML  / LL"]
["20",".11","H","20.27","  ML  / LL"]
["20",".12","H","20.28","  ML  / LL"]
["20",".13","H","20.29","  ML  / LL"]
["20",".14","H","20.30","  ML  / LL"]
["20",".15","H","20.31","  ML  / LL"]
["20",".16","H","20.32","  ML  / LL"]

{"sheet":"K21","index":21,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["21",".01","L","21.01","  ML  / LL"]
["21",".02","L","21.02","  ML  / LL"]
["21",".03","L","21.03","  ML  / LL"]
["21",".04","L","21.04","  ML  / LL"]
["21",".05","L","21.05","  ML  / LL"]
["21",".06","L","21.06","  ML  / LL"]
["21",".07","L","21.07","  ML  / LL"]
["21",".08","L","21.08","  ML  / LL"]
["21",".09","L","21.09","  ML  / LL"]
["21",".10","L","21.10","  ML  / LL"]
["21",".11","L","21.11","  ML  / LL"]
["21",".12","L","21.12","  ML  / LL"]
["21",".13","L","21.13","  ML  / LL"]
["21",".14","L","21.14","  ML  / LL"]
["21",".15","L","21.15","  ML  / LL"]
["21",".16","L","21.16","  ML  / LL"]
["21",".01","H","21.17","  ML  / LL"]
["21",".02","H","21.18","  ML  / LL"]
["21",".03","H","21.19","  ML  / LL"]
["21",".04","H","21.20","  ML  / LL"]
["21",".05","H","21.21","  ML  / LL"]
["21",".06","H","21.22","  ML  / LL"]
["21",".07","H","21.23","  ML  / LL"]
["21",".08","H","21.24","  ML  / LL"]
["21",".09","H","21.25","  ML  / LL"]
["21",".10","H","21.26","  ML  / LL"]
["21",".11","H","21.27","  ML  / LL"]
["21",".12","H","21.28","  ML  / LL"]
["21",".13","H","21.29","  ML  / LL"]
["21",".14","H","21.30","  ML  / LL"]
["21",".15","H","21.31","  ML  / LL"]
["21",".16","H","21.32","  ML  / LL"]

{"sheet":"K22","index":22,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["22",".01","L","22.01","  ML  / LL"]
["22",".02","L","22.02","  ML  / LL"]
["22",".03","L","22.03","  ML  / LL"]
["22",".04","L","22.04","  ML  / LL"]
["22",".05","L","22.05","  ML  / LL"]
["22",".06","L","22.06","  ML  / LL"]
["22",".07","L","22.07","  ML  / LL"]
["22",".08","L","22.08","  ML  / LL"]
["22",".09","L","22.09","  ML  / LL"]
["22",".10","L","22.10","  ML  / LL"]
["22",".11","L","22.11","  ML  / LL"]
["22",".12","L","22.12","  ML  / LL"]
["22",".13","L","22.13","  ML  / LL"]
["22",".14","L","22.14","  ML  / LL"]
["22",".15","L","22.15","  ML  / LL"]
["22",".16","L","22.16","  ML  / LL"]
["22",".01","H","22.17","  ML  / LL"]
["22",".02","H","22.18","  ML  / LL"]
["22",".03","H","22.19","  ML  / LL"]
["22",".04","H","22.20","  ML  / LL"]
["22",".05","H","22.21","  ML  / LL"]
["22",".06","H","22.22","  ML  / LL"]
["22",".07","H","22.23","  ML  / LL"]
["22",".08","H","22.24","  ML  / LL"]
["22",".09","H","22.25","  ML  / LL"]
["22",".10","H","22.26","  ML  / LL"]
["22",".11","H","22.27","  ML  / LL"]
["22",".12","H","22.28","  ML  / LL"]
["22",".13","H","22.29","  ML  / LL"]
["22",".14","H","22.30","  ML  / LL"]
["22",".15","H","22.31","  ML  / LL"]
["22",".16","H","22.32","  ML  / LL"]

{"sheet":"K23","index":23,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["23",".01","L","23.01","  ML  / LL"]
["23",".02","L","23.02","  ML  / LL"]
["23",".03","L","23.03","  ML  / LL"]
["23",".04","L","23.04","  ML  / LL"]
["23",".05","L","23.05","  ML  / LL"]
["23",".06","L","23.06","  ML  / LL"]
["23",".07","L","23.07","  ML  / LL"]
["23",".08","L","23.08","  ML  / LL"]
["23",".09","L","23.09","  ML  / LL"]
["23",".10","L","23.10","  ML  / LL"]
["23",".11","L","23.11","  ML  / LL"]
["23",".12","L","23.12","  ML  / LL"]
["23",".13","L","23.13","  ML  / LL"]
["23",".14","L","23.14","  ML  / LL"]
["23",".15","L","23.15","  ML  / LL"]
["23",".16","L","23.16","  ML  / LL"]
["23",".01","H","23.17","  ML  / LL"]
["23",".02","H","23.18","  ML  / LL"]
["23",".03","H","23.19","  ML  / LL"]
["23",".04","H","23.20","  ML  / LL"]
["23",".05","H","23.21","  ML  / LL"]
["23",".06","H","23.22","  ML  / LL"]
["23",".07","H","23.23","  ML  / LL"]
["23",".08","H","23.24","  ML  / LL"]
["23",".09","H","23.25","  ML  / LL"]
["23",".10","H","23.26","  ML  / LL"]
["23",".11","H","23.27","  ML  / LL"]
["23",".12","H","23.28","  ML  / LL"]
["23",".13","H","23.29","  ML  / LL"]
["23",".14","H","23.30","  ML  / LL"]
["23",".15","H","23.31","  ML  / LL"]
["23",".16","H","23.32","  ML  / LL"]

{"sheet":"K24","index":24,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[[2,1,2,2]]}
["Nødbelysning:",null,null,null,"Bygningsdel:",null,"Tegning:"]
[]
["Kurs:","Adresse: \n01-32",null,"Merking av\n armaturer","Markerings-/\nLedelys:","Bygg / Etasje:","Beskrivelse / Rom #:","Tavle / sikringskurs som tenner armaturen:"]
["24",".01","L","24.01","  ML  / LL"]
["24",".02","L","24.02","  ML  / LL"]
["24",".03","L","24.03","  ML  / LL"]
["24",".04","L","24.04","  ML  / LL"]
["24",".05","L","24.05","  ML  / LL"]
["24",".06","L","24.06","  ML  / LL"]
["24",".07","L","24.07","  ML  / LL"]
["24",".08","L","24.08","  ML  / LL"]
["24",".09","L","24.09","  ML  / LL"]
["24",".10","L","24.10","  ML  / LL"]
["24",".11","L","24.11","  ML  / LL"]
["24",".12","L","24.12","  ML  / LL"]
["24",".13","L","24.13","  ML  / LL"]
["24",".14","L","24.14","  ML  / LL"]
["24",".15","L","24.15","  ML  / LL"]
["24",".16","L","24.16","  ML  / LL"]
["24",".01","H","24.17","  ML  / LL"]
["24",".02","H","24.18","  ML  / LL"]
["24",".03","H","24.19","  ML  / LL"]
["24",".04","H","24.20","  ML  / LL"]
["24",".05","H","24.21","  ML  / LL"]
["24",".06","H","24.22","  ML  / LL"]
["24",".07","H","24.23","  ML  / LL"]
["24",".08","H","24.24","  ML  / LL"]
["24",".09","H","24.25","  ML  / LL"]
["24",".10","H","24.26","  ML  / LL"]
["24",".11","H","24.27","  ML  / LL"]
["24",".12","H","24.28","  ML  / LL"]
["24",".13","H","24.29","  ML  / LL"]
["24",".14","H","24.30","  ML  / LL"]
["24",".15","H","24.31","  ML  / LL"]
["24",".16","H","24.32","  ML  / LL"]